
240W Single Output Industrial DIN Rail Power Supply       EDR-240 series
Features: 
Universal AC input/ full range 
Built-in active PFC function 
Protections: Short circuit/ Over load/ Over voltage/ Over temperature 
Cooling by free air convection 
Can be installed on DIN rail TS-35/7.5 or 15 
LED indicator for power on 
100% full load burn-in test 
Fixed switching frequency at 100KHz 
1 year warranty 

	SPECIFICATIONS

	OUTPUT
	

	Model
	EDR-240-24
	EDR-240-48

	DC Voltage 
	24V
	48V

	Rated Current 
	10A
	5A

	Current Range 
	0-10A
	0-5A

	Rated Power 
	240W
	240W

	Ripple & Noise 
	150mVp-p
	360mVp-p

	Voltage Adj. Range 
	21-28V
	43-53V

	Voltage Tolerance 
	±1%
	±1%

	Setup, Rise Time 
	800ms,40ms/230VAC   800ms,40ms/115VAC at full load

	Hold Up Time 
	24ms/230VAC   24ms/115VAC at full load

	
	

	INPUT
	

	Voltage Range 
	176~264VAC   47~63Hz; 240~370VDC

	AC Current
	2.8A/115V   1.4A/230V

	Efficiency
	84%
	85%

	Inrush Current 
	Cold start 27A/115V   45A/230V

	Leakage Current
	<3.5mA/240VAC

	
	

	PROTECTION
	

	Over Load 
	105%~150% 

	
	Protection type: Constant current limiting, recovers automatically after fault condition is removed

	Over Voltage 
	30-36V
	54-60V

	
	Protection type: Shut down o/p voltage, re-power on to recover

	Over Temp.
	100℃±5℃(TSW1)

	
	Protection type: Shut down o/p voltage, recovers automatically after temperature goes down

	
	

	ENVIRONMENT
	

	Working Temp., Humidity
	-10℃~+70℃; 20%~90%RH

	Storage Temp., Humidity
	-20℃~+85℃; 10%~95%RH

	Vibration
	10~500Hz, 2G 10min./1cycle, period for 60min, each along X, Y, Z axes

	
	

	SAFETY
	

	Withstand Voltage
	I/P-O/P: 3KVAC   I/P-FG: 1.5KVAC   O/P-FG: 0.5KVAC

	Isolation Resistance
	I/P-O/P, I/P-FG, O/P-FG: 100M Ohms / 500VDC

	
	

	STANDARD
	

	EMC Standard
	EN55011,EN55022,EN61000-3-2,-3,EN61000-4-2,3,4,5,6,8,11,ENV50204,EN55024,EN61000-6-2(EN50082-2)

	
	

	OTHERS
	

	Dimension
	63*115*125.2mm(L*W*H)

	Weight
	0.85Kg

	Packing
	20pcs/17.5Kg/1.2CUFT

	
	

	NOTE
	

	1. All parameters NOT specially mentioned are measured at 230VAC input, rated load and 25℃ of ambient temperature. 

2. Ripple & noise are measured at 20MHz of bandwidth by using a 12” twisted pair-wire terminated with a 0.1μ & 47μ parallel capacitor. 

3 .Tolerance: includes set up tolerance, line regulation and load regulation.

4. The power supply is considered a component which will be installed into a final equipment. The final equipment must be re-confirmed that it still meets EMC directives.

5 . Derating may be needed under low input voltages. Please check the derating curve for more details.


[image: image1.jpg]B Mechanical Specification

<
O
O
O
@
O
@)
O

CROBCRORD
RIS
oeeseTese
R
sgesesee
R
SRR
e2e%e% s

(@
@
@
@
@
@
@
@

OCe

Top View

113.5 .
1234

H 1 0000
TB2
+VADJ.6‘*

g @) DCOK O

36

125.2

Side View Front View Side View

Terminal Pin No. Assignment (TB1)
OOOOOOOO PinNo. | Assignment
QOC00000 1 FG O

QOO00000 2 AC/NorDC -
0000000 3 AC/LorDC +

OO0000] Terminal Pin No. Assignment (TB2)
S Pin No. | Assignment

J
OOOOOOOOOO 1,2 | DCOUTPUT-V
- 34 | DCOUTPUT+V

Bottom View

B Installation Instruction

i — 1S | i 1 —— ; This series fits DIN rail TS35/7.5 or TS35/15.
YOO AN CTo . coleey O e For installation details, please refer to the Instruction manual.

g U | ADMISSIBLE DIN-RAIL:TS35/7.5 ORTS35/15
o o (For reference only. Notincluded with unit.)

Back View

File Name:NDR-240-SPEC 2020-01-04





