
60W 120W Single Output Industrial DIN Rail Power Supply         ZDR5 series

	Model
	ZDR5-60-12
	ZDR5-60-24
	ZDR5-120-12
	ZDR5-120-24

	DC Voltage
	12V
	12V
	15V
	24V

	Rated Current
	5A
	2.5A
	10A
	5A

	Current Range
	0 ~ 5A
	0 ~ 2.5A
	0 ~ 10A
	0 ~ 5A

	Rated Power
	60W
	60W
	120W
	120W

	Voltage Adj. Range
	10.8 ~ 13.8V
	21.6 ~ 29V
	10.8 ~ 13.8V
	21.6 ~ 29V

	Voltage Tolerance Note.3
	±2.0%
	±1.0%
	±1.0%
	±1.0%

	Line Regulation
	±1.0%
	±1.0%
	±1.0%
	±1.0%

	Load Regulation
	±1.0%
	±1.0%
	±1.0%
	±1.0%

	Setup, Rise Time
	 600ms/230VAC  600ms/115VAC at full load

	Hold Up Time (Typ.)
	120ms/230VAC 30ms/115VAC at full load

	Voltage Range
	85 ~ 264VAC (277VAC operational ) 120 ~ 370VDC (390VDC operational )

	Frequency Range
	50 ~ 60Hz

	Efficiency (Typ.)
	82%
	86%
	86%
	88%

	AC Current (Typ.)
	1.3A/115VAC 0.7A/230VAC

	Over Load
	105 ~ 160% rated output power

	
	Hiccup mode when output voltage <50%, recovers automatically after fault condition is removed

	
	Constant current limiting within 50% ～100% rated output voltage, recovers automatically after fault condition is removed

	Over Voltage
	14.2 ~ 16.2V
	18.8 ~ 22.5V
	14.2 ~ 16.2V
	18.8 ~ 22.5V

	
	Protection type : Shut down o/p voltage, re-power on to recover

	Working Temp.
	-20 ~ +70℃ (Refer to "Derating Curve")

	Working Humidity
	10% ~ 95%

	Storage Temp., Humidity
	-30 ~ +85℃, 10 ~ 95% RH non-condensing

	Safety Standards
	UL62368-1, UL508, TUV EN61558-2-16, IEC62368-1, EAC TP TC 004, BSMI CNS14336-1 approved; Design refer to EN62368-1

	Dimension
	33*111*89mm (W*H*D)
	40*112*125mm (W*H*D)

	Weight
	236g
	[bookmark: _GoBack]503g

	1. All parameters NOT specially mentioned are measured at 230VAC input, rated load and 25℃ of ambient temperature.

	2. Ripple & noise are measured at 20MHz of bandwidth by using a 12” twisted pair-wire terminated with a 0.1μf & 47μf parallel capacitor.

	3. Tolerance : includes set up tolerance, line regulation and load regulation.

	4. The power supply is considered as an independent unit, but the final equipment still need to re-confirm that the whole system complies with the EMC directives. For guidance on how to perform these EMC tests, please refer to “EMI testing of component power supplies.”

	5. The ambient temperature derating of 3.5℃/1000m with fanless models and of 5℃/1000m with fan models for operating altitude higher than 2000m(6500ft).





