60W 120W Single Output Industrial DIN Rail Power Supply         ZDR5 series

| Model | ZDR5-60-12 | ZDR5-60-24 | ZDR5-120-12 |  | ZDR5-120-24 |
| --- | --- | --- | --- | --- | --- |
| DC Voltage | 12V | 12V | 15V |  | 24V |
| Rated Current | 5A | 2.5A | 10A |  | 5A |
| Current Range | 0 ~ 5A | 0 ~ 2.5A | 0 ~ 10A |  | 0 ~ 5A |
| Rated Power | 60W | 60W | 120W |  | 120W |
| Voltage Adj. Range | 10.8 ~ 13.8V | 21.6 ~ 29V | 10.8 ~ 13.8V |  | 21.6 ~ 29V |
| Voltage Tolerance Note.3 | ±2.0% | ±1.0% | ±1.0% |  | ±1.0% |
| Line Regulation | ±1.0% | ±1.0% | ±1.0% |  | ±1.0% |
| Load Regulation | ±1.0% | ±1.0% | ±1.0% |  | ±1.0% |
| Setup, Rise Time | 600ms/230VAC 600ms/115VAC at full load |  |  |  |  |
| Hold Up Time (Typ.) | 120ms/230VAC 30ms/115VAC at full load |  |  |  |  |
| Voltage Range | 85 ~ 264VAC (277VAC operational ) 120 ~ 370VDC (390VDC operational ) |  |  |  |  |
| Frequency Range | 50 ~ 60Hz |  |  |  |  |
| Efficiency (Typ.) | 82% | 86% | 86% |  | 88% |
| AC Current (Typ.) | 1.3A/115VAC 0.7A/230VAC |  |  |  |  |
| Over Load | 105 ~ 160% rated output power |  |  |  |  |
|  | Hiccup mode when output voltage <50%, recovers automatically after fault condition is removed |  |  |  |  |
|  | Constant current limiting within 50% ～100% rated output voltage, recovers automatically after fault condition is removed |  |  |  |  |
| Over Voltage | 14.2 ~ 16.2V | 18.8 ~ 22.5V | 14.2 ~ 16.2V |  | 18.8 ~ 22.5V |
|  | Protection type : Shut down o/p voltage, re-power on to recover |  |  |  |  |
| Working Temp. | -20 ~ +70℃ (Refer to "Derating Curve") |  |  |  |  |
| Working Humidity | 10% ~ 95% |  |  |  |  |
| Storage Temp., Humidity | -30 ~ +85℃, 10 ~ 95% RH non-condensing |  |  |  |  |
| Safety Standards | UL62368-1, UL508, TUV EN61558-2-16, IEC62368-1, EAC TP TC 004, BSMI CNS14336-1 approved; Design refer to EN62368-1 |  |  |  |  |
| Dimension | 33*111*89mm (W*H*D) |  |  | 40*112*125mm (W*H*D) |  |
| Weight | 236g |  |  | 503g |  |
| 1. All parameters NOT specially mentioned are measured at 230VAC input, rated load and 25℃ of ambient temperature. |  |  |  |  |  |
| 2. Ripple & noise are measured at 20MHz of bandwidth by using a 12” twisted pair-wire terminated with a 0.1μf & 47μf parallel capacitor. |  |  |  |  |  |
| 3. Tolerance : includes set up tolerance, line regulation and load regulation. |  |  |  |  |  |
| 4. The power supply is considered as an independent unit, but the final equipment still need to re-confirm that the whole system complies with the EMC directives. For guidance on how to perform these EMC tests, please refer to “EMI testing of component power supplies.” |  |  |  |  |  |
| 5. The ambient temperature derating of 3.5℃/1000m with fanless models and of 5℃/1000m with fan models for operating altitude higher than 2000m(6500ft). |  |  |  |  |  |